Systems

TM

EleganceTM

###### RS-232 Communications Protocol

# Communications between a Remote PC and the Elegance System:

The Elegance system can communicate with a remote PC over phone lines through a modem and an RS-232 (channel B of UART2).  Communications parameters are 2400 baud, 8 data bits, 1 stop bit and no parity.  This link may be used by a remote PC to program the system with different configurations, retrieve status information from the system, or command the system to perform a certain task.  The Elegance system always acts as a slave to a remote PC, i.e., it always responds to commands from that remote PC.  Upon power up, the modem is initialized by software and configured to answer automatically incoming calls after the number of rings programmed in the 2nd byte of Customer Options (0: disables auto-answer mode, 01-99: range of rings, BCD format).  The modem answers an incoming call after the programmed number of rings (if enabled), and establishes communication with the above parameters.  A remote PC can then proceed to communicate with the system in exactly the same manner as described under "Communications between a PC (Personal Computer) and the Elegance system."  When the calling PC is finished, it should hang up the phone line, after which the Elegance system will terminate its answer session.

Communications between a Third-Party Device and the Elegance System:

The system can communicate with a third-party device through an RS-232 (channel B of UART1). Communications parameters for connector RS232-3 are either 19.2 K baud (if DIP Switch 3 is OFF) or 9.6 K baud (if DIP Switch 3 is ON), 8 data bits, 1 stop bit and no parity. Communications parameters for connector RS232-2 are either 19.2 K baud (if DIP Switch 4 is OFF) or 9.6 K baud (if DIP Switch 4 is ON), 8 data bits, 1 stop bit and no parity.  This link may be used by a third-party device to either send control commands or receive status information regarding both loads and scenes.  The system always acts as a slave to a third-party device, i.e., the system always responds to commands from that third-party device.

Communications between a third-party device to the system always use ASCII code (both directions).  All commands are started with ASCII “^” (ASCII code $5E), followed by a 1-byte command code (ASCII “A” - “J”).  The command may be followed by a number of ASCII digits that varies according to the command used.  The following table shows the currently supported commands, their formats, and response expected, if any.

6414 Hillcrest Park Court  Mobile, AL  36695

Toll Free: 877.466.5483  Telephone: 334.607.9119  Fax: 334.607.9117

www.centralite.com

Command Code		Meaning					Response

and Format

^Annn		Turn On load number nnn.				None

^Bnnn		Turn Off load number nnn.				None

^Cnnn		Turn On scene number nnn.			None

^Dnnn		Turn Off scene number nnn.			None

^Ennnllrr		Move load number nnn to level ll at 		None

rate rr.

^Fnnn		Get level of load number nnn.			ll

^G			Get instant ON/OFF status of all loads.		ddd … d

^H			Get instant ON/OFF status of all switches.	sss … s

^Innn			Press switch number nnn..				None

^Jnnn			Release switch number nnn.			None

nnn is a 3-digit ASCII number specifying either a load number (from 001 to 192), or a scene number (from 001 to 256).

ll is a 2-digit ASCII number specifying load level value (from 00 to 99, where 00 is fully OFF, and 99 is fully ON).

rr is a 2-digit number specifying a code for rate (from 00 to 31) at which a load is activated to the specified level, according to the following table.

“rr”	   Value	“rr”	   Value	“rr”	   Value	“rr”	   Value

00	Immediate	 08	9 seconds	 16	41 seconds	 24	210 seconds

01	1 second	 09	11 seconds	 17	49 seconds	 25	250 seconds

02	2 seconds	 10	13 seconds	 18	60 seconds	 26	300seconds

03	3 seconds	 11	16 seconds	 19	75 seconds	 27	380 seconds

04	4 seconds	 12	19 seconds	 20	90 seconds	 28	450 seconds

05	5 seconds	 13	23 seconds	 21	110 seconds	 29	550 seconds

06	6 seconds	 14	28 seconds	 22	140 seconds	 30	675 seconds

07	7 seconds	 15	34 seconds	 23	175 seconds	 31	800 seconds

ddd … d is a 48-digit ASCII hex number, where every 6-digit entry holds the ON/OFF state of 24 loads (0 for OFF and 1 for ON), as follows.

1st 2 digits (least significant)	bit       0	Load 1

bit	1	Load 2

…

bit	7	Load 8

2nd 2 digits (middle significant)	bit       0	Load 9

bit	1	Load 10

…

bit	7	Load 16

3rd 2 digits (most significant)	bit       0	Load 17

bit	1	Load 18

…

bit	7	Load 24

The order of the 8 load entries is as follows:

LD1, LD2, LD3, ... , LD24  for RLYDRVR 1 (6 digits)

LD1, LD2, LD3, ... , LD24  for RLYDRVR 2 (6 digits)

...

LD1, LD2, LD3, ... , LD24  for RLYDRVR 8 (6 digits)

sss … s is a 96-digit ASCII hex number, where every 4-digit entry holds the ON/OFF state of 16 switches (0 for OFF and 1 for ON), as follows.

1st 2 digits (least significant)	bit       0	STARS 1A

bit	1	STARS 1B

bit	2	STARS 1C

bit	3	STARS 1D

bit	4	STARS 2A

bit	5	STARS 2B

bit	6	STARS 2C

bit	7	STARS 2D

2nd 2 digits (most significant)	bit       0	STARS 3A

bit	1	STARS 3B

bit	2	STARS 3C

bit	3	STARS 3D

bit	4	STARS 4A

bit	5	STARS 4B

bit	6	STARS 4C

bit	7	STARS 4D

The order of the 24 switch entries is as follows:

SW1   for STARS 1A,1B,1C,1D, 2A,2B,2C,2D, 3A,3B,3C,3D, 4A,4B,4C,4D (4 digits)

SW2   for STARS 1A,1B,1C,1D, 2A,2B,2C,2D, 3A,3B,3C,3D, 4A,4B,4C,4D (4 digits)

...

SW24 for STARS 1A,1B,1C,1D, 2A,2B,2C,2D, 3A,3B,3C,3D, 4A,4B,4C,4D (4 digits)

Note that any combination for nnn, ll and rr outside the specified ranges will cause the command to be ignored.  In addition, command ^Ennnllrr will be ignored if it specifies a level other than 00 or 99, or a transition rate other than 00 for non-dimmer loads.

Revised 02/22/01

© CentraLite Systems, Inc.

All Rights Reserved